NSTX Upgrade

Moment Influence Coefficients

NSTXU-CALC-13-05-00

Rev 0

January 18 2011

Prepared By:

___________________________________

Peter Titus, PPPL Analysis Division

Reviewed By:

________________________________________

Bob Woolley, Electrical Engineering

Approved By:

_______________________________________

Ron Hatcher, Electrical Engineering

PPPL Calculation Form

Calculation # 	NSTXU-CALC-13-05-00    Revision #  00		WP #, 1511

(ENG-032)

Purpose of Calculation: (Define why the calculation is being performed.)

Force coefficients are an input to the digital coil protection system (DCPS)[7]. This document is a calculation of the  moment influence coefficients to be applied to the PF currents. Previously, influence coefficients were computed for only radial and axial loads on the coils. There was no adjustment for the force centroid, which could be substantially displaced from the geometric centroid. Where force centers differ from the coil geometric centers, reaction forces at supports may differ significantly from loads computed with the assumption that the forces are at the coil centroid.  Moment coefficients are also being computed by R. Wooley and this calculation may serve as a check for his results, or this calculation may produce coefficients for the DCPS

References (List any source of design information including computer program titles and revision levels.)

Included in the body of the calculations

Assumptions (Identify all assumptions made as part of this calculation.)

Axisymmetry of the coils

Calculation (Calculation is either documented here or attached)

Included in the body of the calculations

Conclusion (Specify whether or not the purpose of the calculation was accomplished.)

Moment influence coefficients have been calculated and tabulated for

checking other's work or inclusion in the DCPS

Cognizant Engineer’s printed name, signature, and date

Phil Heitzenroeder

I have reviewed this calculation and, to my professional satisfaction, it is properly performed and correct.

Checker’s printed name, signature, and date

Ron Hatcher

Table of Contents

Table of Contents										3

Executive Summary									3

Input to the Digital Coil Protection System (DCPS						3

References....................									4

Analysis Code										4

Axisymmetric Analysis Finite Element Model……						4

Results											6

Comparison with Ron Hatcher's  Results							7

Attachment A    Influence Coefficient Subroutine in NTFTM					9

Executive Summary:

It is usual practice to utilize influence coefficient calculations to determine hoop and axial (vertical for tokamak's) loads from coil currents. However the centroid of the Lorentz loads may not be at the geometric center of the coils. Where there is significant offset between the Lorentz centroid and the geometric center, there will be a moment about the coil geometric center in addition to the net loads. This may be a significant contributor to the support reaction loads and to the stresses in the coils themselves. In design and analysis of coil systems, distributions  of fields and forces are typically calculated for a useful structural/magnetic mesh which is typically fine enough to properly distribute the Lorentz forces and resolve any moments about the coil current centers. When influence coefficients are used in operating tokamaks to check coil stresses and support loading the effect of moments has been omitted. To the author's knowledge, this is true of Alcator C-Mod, TFTR and NSTX . Addition of the moment coefficients completes the three degrees of freedom available from the axisymmetric analysis of ring coils.

Digital Coil Protection System (DCPS) Input

The proposed DCPS is described in detail in a draft requirements document by Robert Woolley ref [7]. Force influence coefficients are already included in plans for the DCPS. Inclusion of these moment coefficients is proposed, depending on their usefulness in quantifying stresses for specific components. In the description of the DCPS, the “systems code” will actually be the analyses described in the filed structural calculations. There is a global model which is the closest thing we have to a single systems code, but this is augmented in many ways by separate calculations to address specific stress locations and components and support hardware. During the final design activity,  Each preparer of a calculation will be assigned the development of “mini algorithms” These may make use of moment influence coefficients. One examples is:

.

PF 2,3 supports, welds bolts – At this stage, these are  just calculated from influence coefficient matrix loads divided by weld or bolt area. Addition of moment influence coefficients adds overturning moments to the calculation of the bolt loads .

References

[1] NSTX Influence Coefficients,  calculation # NSTXU  13 03-00,  Ron Hatcher  DATE: July 9 2009

[2] NSTX-CALC-13-001-00 Rev 1  Global Model – Model Description, Mesh Generation, Results, Peter H. Titus  December  2010

[3] NSTX Structural Design Criteria Document, NSTX_DesCrit_IZ_080103.doc I. Zatz

[4] NSTX Design Point Sep 8 2009  http://www.pppl.gov/~neumeyer/NSTX_CSU/Design_Point.html

[5] OOP PF/TF Torques on TF , R. Woolley, NSTXU CALC 132-03-00

[6] "MHD and Fusion Magnets, Field and Force Design Concepts", R.J.Thome, John Tarrh, Wiley Interscience, 1982

[7] DIGITAL COIL PROTECTION SYSTEM (DCPS) REQUIREMENTS DOCUMENT (DRAFT), NSTX-CSU-RD-DCPS for the National Spherical Torus Experiment Center Stack Upgrade, February 5, 2010 R. Woolley

[8] "MHD and Fusion Magnets, Field and Force Design Concepts", R.J.Thome, John Tarrh, Wiley Interscience, 1982

[9] NSTX-CALC-13-001-00, Global Model – Model Description, Mesh Generation, Results

[10]   NSTXU-CALC-132-04-00  ANALYSIS OF TF OUTER LEG, Han Zhang,  August 31, 2009

Analysis Code, NTFTM

Mesh generation , calculation of the Lorentz forces, and generation of the influence coefficients  is done  using a code written by the author of this report. The influence coefficient subroutine is included as appendix A The mesh generation feature of the code is checked visually  and within ANSYS during the PREP7 geometry check. . The authors code uses elliptic integrals for 2D field calculations, and   Biot Savart solution for 3D field calculations. These are based 2D formulations, and  single stick field calculations from Dick Thomes book [8] with some help from Pillsbury’s FIELD3D code to catch all the coincident current vectors, and other singularities.

The code in various forms has been used for 20 years and is suitable for structural calculations. It is also being used for calculation of load files in an NSTX global model[9]. Recent checks include NSTX out-of-plane load comparisons with ANSYS [10] and MAXWELL and calculations of trim coil fields for W7X compared with Neil Pomphrey's calculations.  The analysts in the first ITER EDA went through an exercise to compare loads calculated by the US (using this code), RF and by Cees Jong in ANSYS, and agreements were  good.  Some information on the code, named FTM (Win98) and NTFTM2 (NT,XP),  is available at: http://198.125.178.188/ftm/manual.pdf  ).

Axisymmetric Analysis Model

Computation of influence coefficients is done by computing contributions of fields and forces in one element group with respect to other element groups. The element groups are identified by real constant numbers for the elements in the group. This allows coils or sections of coils to be considered in the matrix calculation. For this calculation, the element designations used by Ron Hatcher's calculation [1] have been used to allow a comparison with the force influence coefficients. Moment coefficients require the computation of the force contributions with a running summation of forces multiplied by the element force times the appropriate radial or axial lever arm with respect to the element group centroid. So computation of the moment influence coefficients also produces the force influence coefficients.

Figure 2 Axisymmetric Models

Results

Moment Influence Coefficients

Comparison with Ron’s Radial Influence Coefficients

(Titus)

(Hatcher ref [1] )

Attachment A Influence Coefficient Subroutine

Subroutine Influence(numcoils)

include 'scommon.blk'

DIMENSION rinffx(50,50)

DIMENSION rinffy(50,50)

DIMENSION rinfmz(50,50)

do 9 i=1,50

do 9 j=1,50

rinffx(i,j)=0

rinffy(i,j)=0

rinfmz(i,j)=0

9   Continue

do 10 i=1,numcoils

do 10 j=1,numcoils

call snal(0)

call seal(0)

ia1=1

ia2=2

ia3=3

ia4=4

ib1=0

ib2=0

ib3=0

ib4=0

CALL Sreal(i,i)

CALL Sreal(j,i)

call SNELEM(i,i)

typekeydum=typekey

typekey=7

egrpkeydum=egrpkey

egrpkey=7

r=0.0

call CCUR(R,i,ia1,ia2,ia3,ia4,ib1,ib2,ib3,ib4)

call stype(7,70)

call snelem(70,70)

call sfield(i)

call snal(0)

call seal(0)

call stype(7,70)

call gerase(70)

call reduce

CALL Sreal(i,i)

call SNELEM(i,i)

CALL Sreal(j,j)

call SNELEM(j,j)

call mfor(i,ia1,ia2,ia3,ia4,ib1,ib2,ib3,ib4)

call mfsum(i,i,fxsum,fysum,xmzsum)

rinffx(i,j)=fxsum

rinffy(i,j)=fysum

rinfmz(i,j)=xmzsum

bxs=0.0

bys=0.0

byz=0.0

call bscale(i,bxs,bys,bzs)

call fscale(i,bxs,bys,bzs)

call bscale(j,bxs,bys,bzs)

call fscale(j,bxs,bys,bzs)

10   CONTINUE

54   CONTINUE

do 15 i=1,numcoils

do 15 j=1,numcoils

if (i.ne.j) rinffx(i,j)=rinffx(i,j)-rinffx(i,i)

rinffy(i,j)=rinffy(i,j)-rinffy(i,i)

rinfmz(i,j)=rinfmz(i,j)-rinfmz(i,i)

15   Continue

write(7,*) 'FX Influence Matrix N/rad'

do 11 i=1,numcoils

write(7,*) i,rinffx(i,1),rinffx(i,2),rinffx(i,3),rinffx(i,4),

c rinffx(i,5),rinffx(i,6),rinffx(i,7),rinffx(i,8),rinffx(i,9),

c rinffx(i,10),rinffx(i,11),rinffx(i,12),rinffx(i,13),rinffx(i,14),

c rinffx(i,15),rinffx(i,16),rinffx(i,17),rinffx(i,18),rinffx(i,19)

11   continue

write(7,*) 'FY Influence Matrix N/rad'

do 12 i=1,numcoils

write(7,*) i,rinffy(i,1),rinffy(i,2),rinffy(i,3),rinffy(i,4),

c rinffy(i,5),rinffy(i,6),rinffy(i,7),rinffy(i,8),rinffy(i,9),

c rinffy(i,10),rinffy(i,11),rinffy(i,12),rinffy(i,13),rinffy(i,14),

c rinffy(i,15),rinffy(i,16),rinffy(i,17),rinffy(i,18),rinffy(i,19)

12   continue

write(7,*) 'MZ Influence Matrix N-m/rad'

do 13 i=1,numcoils

write(7,*) i,rinfmz(i,1),rinfmz(i,2),rinfmz(i,3),rinfmz(i,4),

c rinfmz(i,5),rinfmz(i,6),rinfmz(i,7),rinfmz(i,8),rinfmz(i,9),

c rinfmz(i,10),rinfmz(i,11),rinfmz(i,12),rinfmz(i,13),rinfmz(i,14),

c rinfmz(i,15),rinfmz(i,16),rinfmz(i,17),rinfmz(i,18),rinfmz(i,19)

13   continue

do 16 i=1,numcoils

do 16 j=1,numcoils

rinffx(i,j)=rinffx(i,j)*.2248*2*3.1416

rinffy(i,j)=rinffy(i,j)*.2248*2*3.1416

rinfmz(i,j)=rinfmz(i,j)*.2248*2*3.1416*39.37

16   Continue

write(7,*) 'FX Influence Matrix lb/coil'

do 17 i=1,numcoils

write(7,*) i,rinffx(i,1),rinffx(i,2),rinffx(i,3),rinffx(i,4),

c rinffx(i,5),rinffx(i,6),rinffx(i,7),rinffx(i,8),rinffx(i,9),

c rinffx(i,10),rinffx(i,11),rinffx(i,12),rinffx(i,13),rinffx(i,14),

c rinffx(i,15),rinffx(i,16),rinffx(i,17),rinffx(i,18),rinffx(i,19)

17   continue

write(7,*) 'FY Influence Matrix lb/coil'

do 18 i=1,numcoils

write(7,*) i,rinffy(i,1),rinffy(i,2),rinffy(i,3),rinffy(i,4),

c rinffy(i,5),rinffy(i,6),rinffy(i,7),rinffy(i,8),rinffy(i,9),

c rinffy(i,10),rinffy(i,11),rinffy(i,12),rinffy(i,13),rinffy(i,14),

c rinffy(i,15),rinffy(i,16),rinffy(i,17),rinffy(i,18),rinffy(i,19)

18   continue

write(7,*) 'MZ Influence Matrix in-lb/coil'

do 19 i=1,numcoils

write(7,*) i,rinfmz(i,1),rinfmz(i,2),rinfmz(i,3),rinfmz(i,4),

c rinfmz(i,5),rinfmz(i,6),rinfmz(i,7),rinfmz(i,8),rinfmz(i,9),

c rinfmz(i,10),rinfmz(i,11),rinfmz(i,12),rinfmz(i,13),rinfmz(i,14),

c rinfmz(i,15),rinfmz(i,16),rinfmz(i,17),rinfmz(i,18),rinfmz(i,19)

19   continue

typekey=typekeydum

egrpkey=egrpkeydum

return

end

# Text boxes

Figure 1